## Heating Sizing
Simple Heating System Size: Washington State
This heating system sizing calculator is based on the Prescriptive Requirements of the 2018 and 2021 Washington State Energy Code (WSEC) . This tool will calculate heating loads only. ACCA procedures for sizing cooling systems should be used to determine cooling loads. Please complete the green drop-downs and boxes that are applicable to your project. As you make selections in the drop-downs for each section, some values will be calculated for you. If you do not see the selection you need in the drop-down options, please contact the WSU Energy Program at energycode@energy.wsu.edu or (360) 956-2042 for assistance.
This tool is for the permitting purposes only. A Manual J calculation is required to meet the requirement of the Washington State Energy Code.
| Project Information | [7 empty] | Contact Information
Heating System Type:
To see detailed instructions for each section, place your cursor on the word "Instructions"
|  | Design Temperature | [6 empty] | Deisgn Temperature |  |  |  |  | _______
|  |  |  | Instructions |  |  | Select closest city |  | Design Temperature Difference (∆T) |  |  |  |  | _______
∆T = Indoor (70 degrees) - Outdoor Design Temp
Area of Building
Conditioned Floor Area
|  |  |  | Instructions |  | Conditioned Floor Area (sq ft)
|  |  | Average Ceiling Height | [7 empty] | Conditioned Volume
|  |  |  | Instructions |  | Average Ceiling Height (ft) |  |  | 8.5 |  | ________
|  | Glazing and Doors | [6 empty] | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | Select U-Factor |  | No selection |  |  |  | --
|  | Skylights | [6 empty] | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  |  |  | 0.5 |  |  |  | 0
Insulation
|  |  | Attic | [5 empty] | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Single Rafter or Joist Vaulted Ceilings | [5 empty] | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Above Grade Walls (see Figure 1) | [5 empty] | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Floors | [5 empty] | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Below Grade Walls and Slabs (see Figure 1) | [5 empty] | Wall U-Factor | X | Area |  | UA
|  |  |  | Instructions | Wall & Slab |  | Select Wall & Slab Insulation |  | No Selection |  |  |  | --
[5 empty] | Depth |  | Select nearest slab depth |  | Slab F-Factor | X | Length |  | UA
[9 empty] | -- |  |  |  | --
|  |  | Slab on Grade (see Figure 1) | [5 empty] | F-Factor | X | Length |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
Location of Ducts
|  |  |  | Instructions |  |  | Select Location of Ducts |  |  |  | Duct Leakage Coefficient
No Selection
[8 empty] | Sum of UA |  |  |  |  | _________
[8 empty] | Envelope Heat Load |  |  |  |  | _________ | Btu / Hour
Sum of UA x ∆T
[8 empty] | Air Leakage Heat Load |  |  |  |  | _________ | Btu / Hour
Volume x 0.6 x ∆T x 0.018
[8 empty] | Building Design Heat Load |  |  |  |  | _________ | Btu / Hour
Air leakage + envelope heat loss
[8 empty] | Building and Duct Heat Load |  |  |  |  | _________ | Btu / Hour
Ducts in unconditioned space: sum of building heat loss x 1.10
Ducts in conditioned space: sum of building heat loss x 1
[8 empty] | Maximum Heat Equipment Output |  |  |  |  | _________ | Btu / Hour
Building and duct heat loss x 1.40 for forced air furnace
Building and duct heat loss x 1.25 for heat pump
Note on G13: Using the drop-down, select the city that is closest to your building site.
Note on G18: Using exterior measurements, enter the square footage of living space conditioned directly or indirectly.
Note on G21: Enter the average ceiling height from your building plans.
Note on G24: Calculate and enter the total area of the vertical fenestration products (windows and doors) in the structure. Example: Window #1 area 10 ft2 Window #2 area 15 ft2 Total area 25 ft2 The glazing and doors portion of this calculator assumes the installed glazing products have an area weighted average U-factor
Note on G26: Calculate and enter the total area of the skylights in the structure. Example: Skylight #1 area 10 ft2 Skylight #2 area 15 ft2 Total area 25 ft2 The skylight portion of this calculator assumes the installed skylight products have an area weighted average U-factor of 0.30.
Note on G30: Using the drop-down, select the R-value specified in your building plans for flat and/or scissor truss ceilings. Then calculate and enter the area of the ceiling under attic insulated with the selected R-value.
Note on G33: Using the drop-down, select the R-value specified in your building plans for vaulted ceilings. Then calculate and enter the area of the vaulted ceiling insulated with the selected R-value. If there are no vaulted ceilings, select "No Vaulted Ceilings in this project"
Note on G36: Using the drop-down, select the R-value specified in your building plans for the above grade walls. Then calculate and enter the net above grade wall area. Net above grade wall area is the total above grade wall area minus the area of windows and doors. See Figure 1 for help understanding above and below grade.
Note on G39: Using the drop-down, select the R-value specified in your building plans for floors above unconditioned spaces. Then calculate and enter the floor area with the selected R-value.
Note on G42: Below-Grade Wall and Slab Description Using the drop-down, select the insulation specified in your building plans for below grade walls and slabs. Next, using the drop down select the depth (2', 3.5' or 7') that is nearest to the average depth below-grade of your slab. Below-Grade Wall Area: Calculate and enter the net below grade wall area. Net below grade wall area is the total below grade wall area minus the area of windows and doors. Slab Perimeter Calculate and enter the linear feet of perimeter of the slab below grade. For example, if the basement floor is a 54' x 32' slab below grade, the linear perimeter would be 172ft . 54'+54'+32'+32' = 172'
Note on G47: Using the drop-down, select the R-value specified in your building plans for slab on grade. Then calculate and enter the linear feet of perimeter of the slab on grade. For example, if the living room is a 20' x 30' slab on grade, the linear perimeter would be 100 ft. 20'+20'+30'+30'=100'
Note on G51: Using the drop-down, indicate if the majority of ducts will be installed in conditioned or unconditioned spaces. - If the majority of ducts will be installed in living areas, or if the heating system will be ductless, select "Conditioned Space" - If the majority of ducts will be installed in unconditioned space (crawlspace or unconditioned basement), select "Unconditioned Space"
Above Grade
Below Grade
Figure 1.
All Other Systems
Heat Pump

## LookUps (hidden)
Each of these sections contain on row 2 the result of the selections, and three columns: a lookup number for formulas, selections for drop down boxes, and the measurement to use in the formulas.
Below Grade Walls and Slabs
Indoor Design Temperature |  | Outdoor Design Temperature |  |  | Vertical Glazing and Doors |  |  | Attic |  |  | Single Rafter or Joist Vaulted Ceilings |  |  | Above Grade Walls |  |  | Floors |  |  |  | Selection |  | Slab on Grade |  |  | Location of Ducts |  | Heating System Type | 2 | Linked to selection in row
[20 empty] | Wall & Slab | Select Wall & Slab Insulation
70 | Column1 | City | Temp | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor |  | Depth | Select nearest slab depth | Column1 | R-Value | F-Factor | Offset | location of ducts | Heat loss correction
| 1 | Select closest city |  | 1 | Select U-Factor | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection |  | Search String | Select Wall & Slab Insulation, Select nearest slab depth | 1 | Select R-Value | No selection | 1 | Select Location of Ducts | No Selection | Forced Air Furnace | 1 | 1.4
| 2 | Aberdeen 20 NNE | 25 | 2 | None | -- | 2 | None | -- | 2 | None | -- | 2 | None | -- | 2 | None | -- |  | U | #N/A | 2 | None | -- | 2 | Conditioned Space | 1 | Heat Pump | 2 | 1.25
| 3 | Anacortes | 24 | 3 | U-0.30 | 0.3 | 3 | R-60 | 0.024 | 3 | R-38 | 0.026 | 3 | R-20 STD +R-5 ci | 0.045 | 2 | R-30 | 0.029 |  | F | #N/A | 3 | R-10 2' Perimeter | 0.54 | 3 | Unconditioned Space | 1.1
| 4 | Anatone | -4 | 4 | U-0.29 | 0.29 | 4 | R-60 Advanced | 0.17 | 4 | R-49 | 0.02 | 4 | R-13 STD +R-10 ci | 0.045 | 3 | R-38 | 0.025 |  |  |  | 4 | R-10 Fully Insulated | 0.36 | 4 | No Ducts | 1
| 5 | Appleton | 11 | 5 | U-0.28 | 0.28 | 5 | R-49 | 0.026 | 5 | R-60 | 0.017 | 5 | R-21 Intermediate | 0.056 | 4 | R-48 | 0.02 |  |  |  | 5 | R-10 4' Vertical | 0.48
| 6 | Auburn | 25 | 6 | U-0.27 | 0.27 | 6 | R-49 Advanced | 0.02 | 6 | No Vaulted Ceilings in this project. | --- | 6 | R-23 Intermediate | 0.054 | 5 | No Floors above unconditioned spaces. | --- |  | DropDown_BelowGradeWalls |  | 6 | R10 4' Horizontal w/TB | 0.48
| 7 | Battleground | 19 | 7 | U-0.26 | 0.26 | 7 | R-38 | 0.031 |  |  |  | 7 | R-21 INT plus R-4 ci | 0.043 |  |  |  |  | Select Wall & Slab Insulation |  | 7 | No Slab on Grade in this project. | ---
| 8 | Bellevue | 24 | 8 | U-0.25 | 0.25 | 8 | R-38 Advanced | 0.026 |  |  |  | 8 | R-21 INT plus R-5 ci | 0.041 |  |  |  |  | None
| 9 | Bellingham 2N | 19 | 9 | U-0.24 | 0.24 | [6 empty] | 9 | R-21 INT plus R-12 ci | 0.032 |  |  |  |  | R0 Uninsulated
| 10 | Benton City 2 NW | 11 | 10 | U-0.23 | 0.23 | [6 empty] | 10 | R-21 INT plus R-16 ci | 0.028 |  |  |  |  | R10 Foam Ext
| 11 | Bickleton | 4 | 11 | U-0.22 | 0.22 | [13 empty] | R11 Batt
| 12 | Blaine | 17 | 12 | U-0.21 | 0.21 | [13 empty] | R12 Foam Ext
| 13 | Bothell 2 N | 17 | 13 | U-0.20 | 0.2 | [13 empty] | R13 Batt + R5 ci
| 14 | Bremerton | 29 | 14 | U-0.19 | 0.19 | [13 empty] | R10 Foam Ext w/TB, R10 Full Underslab
| 15 | Brier | 24 | 15 | U-0.18 | 0.18 | [13 empty] | R20 Foam Ext w/TB, R10 Full Underslab
| 16 | Buckley 1 NE | 26 | [16 empty] | R19 Batt w/TB
| 17 | Bumping Lake | -5 | [16 empty] | R21 Batt w/TB
| 18 | Burlington | 19
| 19 | Camas | 21 | [16 empty] | DropDown_SlabDepth
| 20 | Castle Rock | 23 | [16 empty] | Select nearest slab depth
| 21 | Cedar Lake | 20 | [16 empty] | 2' depth
| 22 | Centralia | 21 | [16 empty] | 3.5' depth
| 23 | Central Park | 27 | [16 empty] | 7' depth
| 24 | Chehalis | 21
| 25 | Chelan | 10
| 26 | Cheney | 4
| 27 | Chesaw | -11
| 28 | Chewalah 2 S | -9
| 29 | Chief Joseph Dam | 6
| 30 | Clallam Bay 1 NNE | 28
| 31 | Clarkston | 10
| 32 | Clearbrook | 19
| 33 | Clearwater | 26
| 34 | Cle Elum | 1
| 35 | Clyde Hill | 24
| 36 | Colfax 1 NW | 2
| 37 | College Place | 6
| 38 | Colville AP | -2
| 39 | Conconully | -7
| 40 | Concrete | 19
| 41 | Connell 4 NNW | 6
| 42 | Cougar 5 E | 25
| 43 | Coulee Dam 1 SW | 9
| 44 | Coupeville 1 S | 21
| 45 | Cushman Dam | 22
| 46 | Dallesport AP | 14
| 47 | Darrington RS | 13
| 48 | Davenport | 5
| 49 | Dayton 1 WSW | 5
| 50 | Deer Park 2 E | -5
| 51 | Des Moines | 25
| 52 | Diablo Dam | 15
| 53 | Dishman | 9
| 54 | East Bremerton | 29
| 55 | Edmonds | 24
| 56 | Electron Headwks | 16
| 57 | Ellensburg AP | 2
| 58 | Elma | 24
| 59 | Eltopia 6 W | 9
| 60 | Elwha RS | 24
| 61 | Enumclaw | 26
| 62 | Ephrata AP | 7
| 63 | Everett JC | 23
| 64 | Everett Paine AFB | 21
| 65 | Fircrest | 29
| 66 | Forks I E | 23
| 67 | Fort Lewis | 24
| 68 | Fruitvale | 1.1
| 69 | Glacier RS | 13
| 70 | Glenoma (Kosmos) | 18
| 71 | Goldendale | 7
| 72 | Grandview | 12
| 73 | Grapeview | 30
| 74 | Grayland 2 S | 28
| 75 | Grays River Hatchery | 24
| 76 | Greenwater | 1.4
| 77 | Grotto | 21
| 78 | Harrington 2 S | 3
| 79 | Hartline | 7
| 80 | Hatton 8 E | 1
| 81 | Holden Village | 4
| 82 | Hoquiam AP | 26
| 83 | Ice Harbor Dam | 17
| 84 | Inchelium 2 NW | 0
| 85 | Issaquah | 23
| 86 | John Day Dam | 19
| 87 | Kelso AP | 24
| 88 | Kennewick 10 SW | 13
| 89 | Kent | 21
| 90 | Kid Valley | 20
| 91 | Kirkland | 17
| 92 | Lacey | 17
| 93 | Lacrosse 3 ESE | -3
| 94 | La Grande | 23
| 95 | Lake Cle Elum | -4
| 96 | Lake Forest Park | 20
| 97 | Lake Kachess | -2
| 98 | Lake Keechelus | 0
| 99 | Lakewood Center | 23
| 100 | Landsburg | 18
| 101 | Larson AFB | 6
| 102 | Laurier | -8
| 103 | Leavenworth | -3
| 104 | Lemanasky Lake | -7
| 105 | Lind 3 NE | 6
| 106 | Linwood | 10
| 107 | Little Goose Dam | 22
| 108 | Long Beach 3 NNE | 25
| 109 | Longview | 24
| 110 | Lower Granite Dam | 14
| 111 | Lower Monument Dam | 18
| 112 | Lynden | 18
| 113 | Lynnwood | 24
| 114 | Maloft | 4
| 115 | Marietta 3 NNW | 18
| 116 | Marysville | 23
| 117 | McMillin Res. | 21
| 118 | McNary Dam | 11
| 119 | Medical Lake | 4
| 120 | Medina | 24
| 121 | Mercer Island | 25
| 122 | Metaline Falls | -1
| 123 | Methow 2 W | 1
| 124 | Mountlake Terrace | 22
| 125 | Mt. Spokane Summit | -2
| 126 | Mount Vernon 3 WNW | 20
| 127 | Moxee City 10 E | 8
| 128 | Mud Mtn. Dam | 23
| 129 | Nespelem 2 S | -4
| 130 | Newhalem | 19
| 131 | Newport | -5
| 132 | Normandy Park | 24
| 133 | Northport | 2
| 134 | Oak Harbor | 16
| 135 | Oakville | 20
| 136 | Odessa | 7
| 137 | Olga 2 SE | 24
| 138 | Olympia, AP. | 17
| 139 | Omak 2 NW | 3
| 140 | Opportunity | 8
| 141 | Oroville | 5
| 142 | Othello | 9
| 143 | Packwood | 16
| 144 | Palmer 3 SE | 22
| 145 | Parkland | 20
| 146 | Pasco | 13
| 147 | Plain | -3
| 148 | Pleasant View | 16
| 149 | Pt. Grenville | 27
| 150 | Pomeroy | 3
| 151 | Port Angeles | 28
| 152 | Port Orchard | 29
| 153 | Port Townsend | 25
| 154 | Priest Rapids Dam | 14
| 155 | Prosser | 12
| 156 | Pullman Exp. Sta. | 1
| 157 | Puyallup | 19
| 158 | Quilcene 2 SW | 23
| 159 | Quillayute AP | 23
| 160 | Quinault RS | 25
| 161 | Quincy 1 NE | 4
| 162 | Rainier, Longmire | 15
| 163 | Paradise RS | 8
| 164 | Raymond | 28
| 165 | Redmond | 17
| 166 | Renton | 24
| 167 | Republic | -9
| 168 | Richland | 11
| 169 | Rimrock Tieton Dam | 4
| 170 | Ritzville | 6
| 171 | Rosalia | 6
| 172 | Ross Dam | 14
| 173 | St. John | 15
| 174 | Sappho 8 E | 23
| 175 | Satus Pass | 10
| 176 | Seattle: Sea-Tac AP | 24
| 177 | Sedro Woolley 1 E | 19
| 178 | Selah | 11
| 179 | Sequim | 23
| 180 | Shelton | 23
| 181 | Shoultes | 23
| 182 | Skamania Fish Hatch. | 24
| 183 | Smyrna | 8
| 184 | Snohomish | 21
| 185 | Snoqualmie Falls | 22
| 186 | Snoqualmie Pass | 6
| 187 | South Broadway | 11
| 188 | So. Olympic Tree Farm | 24
| 189 | Spanaway | 20
| 190 | Spokane AP | 4
| 191 | Spokane CO | 10
| 192 | Spokane Fairchild AFB | 4
| 193 | Sprague | 4
| 194 | Stampede Pass | 7
| 195 | Startup 1 E | 20
| 196 | Stehekin 3 NW | 12
| 197 | Steilacoom | 21
| 198 | Stevens Pass | 6
| 199 | Stockdill Ranch | -14
| 200 | Sumner | 19
| 201 | Sunnyside | 12
| 202 | Tacoma McChord | 21
| 203 | Tacoma CO | 29
| 204 | Tatoosh Island | 31
| 205 | Thompson Place | 20
| 206 | Tietort Intake | 6
| 207 | Toledo AP | 17
| 208 | Toppenish | 11
| 209 | Trinidad 2 SSE | 13
| 210 | Tukwila | 24
| 211 | Tumwater | 17
| 212 | University Place | 29
| 213 | Upper Baker Dam | 14
| 214 | Vancouver | 22
| 215 | Vashon Island | 28
| 216 | Walla Walla AP | 6
| 217 | Walla Walla CO | 13
| 218 | Wapato | 10
| 219 | Washougal 8 ENE | 21
| 220 | Waterville | 1
| 221 | Wawawai 2 NW | 14
| 222 | Wellpinit | 1
| 223 | Wenatchee AP | 13
| 224 | Wenatchee CO | 10
| 225 | West Clarkston | 10
| 226 | Whidbey Island | 11
| 227 | White River RS | 12
| 228 | White Swan RS | 8
| 229 | Whitman Mission | 11
| 230 | Wilbur | 4
| 231 | Willapa Harbor | 26
| 232 | Wilson Creek | 3
| 233 | Wind River | 15
| 234 | Winthrop 1 WSW | -12
| 235 | Yakima AP | 11

## Weather Data (hidden)
Select closest city
Aberdeen 20 NNE | 25
Anacortes | 24
Anatone | -4
Appleton | 11
Auburn | 25
Battleground | 19
Bellevue | 24
Bellingham 2N | 19
Benton City 2 NW | 11
Bickleton | 4
Blaine | 17
Bothell 2 N | 17
Bremerton | 29
Brier | 24
Buckley 1 NE | 26
Bumping Lake | -5
Burlington | 19
Camas | 21
Castle Rock | 23
Cedar Lake | 20
Centralia | 21
Central Park | 27
Chehalis | 21
Chelan | 10
Cheney | 4
Chesaw | -11
Chewalah 2 S | -9
Chief Joseph Dam | 6
Clallam Bay 1 NNE | 28
Clarkston | 10
Clearbrook | 19
Clearwater | 26
Cle Elum | 1
Clyde Hill | 24
Colfax 1 NW | 2
College Place | 6
Colville AP | -2
Conconully | -7
Concrete | 19
Connell 4 NNW | 6
Cougar 5 E | 25
Coulee Dam 1 SW | 9
Coupeville 1 S | 21
Cushman Dam | 22
Dallesport AP | 14
Darrington RS | 13
Davenport | 5
Dayton 1 WSW | 5
Deer Park 2 E | -5
Des Moines | 25
Diablo Dam | 15
Dishman | 9
East Bremerton | 29
Edmonds | 24
Electron Headwks | 16
Ellensburg AP | 2
Elma | 24
Eltopia 6 W | 9
Elwha RS | 24
Enumclaw | 26
Ephrata AP | 7
Everett JC | 23
Everett Paine AFB | 21
Fircrest | 29
Forks I E | 23
Fort Lewis | 24
Fruitvale | 1.1
Glacier RS | 13
Glenoma (Kosmos) | 18
Goldendale | 7
Grandview | 12
Grapeview | 30
Grayland 2 S | 28
Grays River Hatchery | 24
Greenwater | 1.4
Grotto | 21
Harrington 2 S | 3
Hartline | 7
Hatton 8 E | 1
Holden Village | 4
Hoquiam AP | 26
Ice Harbor Dam | 17
Inchelium 2 NW | 0
Issaquah | 23
John Day Dam | 19
Kelso AP | 24
Kennewick 10 SW | 13
Kent | 21
Kid Valley | 20
Kirkland | 17
Lacey | 17
Lacrosse 3 ESE | -3
La Grande | 23
Lake Cle Elum | -4
Lake Forest Park | 20
Lake Kachess | -2
Lake Keechelus | 0
Lakewood Center | 23
Landsburg | 18
Larson AFB | 6
Laurier | -8
Leavenworth | -3
Lemanasky Lake | -7
Lind 3 NE | 6
Linwood | 10
Little Goose Dam | 22
Long Beach 3 NNE | 25
Longview | 24
Lower Granite Dam | 14
Lower Monument Dam | 18
Lynden | 18
Lynnwood | 24
Maloft | 4
Marietta 3 NNW | 18
Marysville | 23
McMillin Res. | 21
McNary Dam | 11
Medical Lake | 4
Medina | 24
Mercer Island | 25
Metaline Falls | -1
Methow 2 W | 1
Mountlake Terrace | 22
Mt. Spokane Summit | -2
Mount Vernon 3 WNW | 20
Moxee City 10 E | 8
Mud Mtn. Dam | 23
Nespelem 2 S | -4
Newhalem | 19
Newport | -5
Normandy Park | 24
Northport | 2
Oak Harbor | 16
Oakville | 20
Odessa | 7
Olga 2 SE | 24
Olympia, AP. | 17
Omak 2 NW | 3
Opportunity | 8
Oroville | 5
Othello | 9
Packwood | 16
Palmer 3 SE | 22
Parkland | 20
Pasco | 13
Plain | -3
Pleasant View | 16
Pt. Grenville | 27
Pomeroy | 3
Port Angeles | 28
Port Orchard | 29
Port Townsend | 25
Priest Rapids Dam | 14
Prosser | 12
Pullman Exp. Sta. | 1
Puyallup | 19
Quilcene 2 SW | 23
Quillayute AP | 23
Quinault RS | 25
Quincy 1 NE | 4
Rainier, Longmire | 15
Paradise RS | 8
Raymond | 28
Redmond | 17
Renton | 24
Republic | -9
Richland | 11
Rimrock Tieton Dam | 4
Ritzville | 6
Rosalia | 6
Ross Dam | 14
St. John | 15
Sappho 8 E | 23
Satus Pass | 10
Seattle: Sea-Tac AP | 24
Sedro Woolley 1 E | 19
Selah | 11
Sequim | 23
Shelton | 23
Shoultes | 23
Skamania Fish Hatch. | 24
Smyrna | 8
Snohomish | 21
Snoqualmie Falls | 22
Snoqualmie Pass | 6
South Broadway | 11
So. Olympic Tree Farm | 24
Spanaway | 20
Spokane AP | 4
Spokane CO | 10
Spokane Fairchild AFB | 4
Sprague | 4
Stampede Pass | 7
Startup 1 E | 20
Stehekin 3 NW | 12
Steilacoom | 21
Stevens Pass | 6
Stockdill Ranch | -14
Sumner | 19
Sunnyside | 12
Tacoma McChord | 21
Tacoma CO | 29
Tatoosh Island | 31
Thompson Place | 20
Tietort Intake | 6
Toledo AP | 17
Toppenish | 11
Trinidad 2 SSE | 13
Tukwila | 24
Tumwater | 17
University Place | 29
Upper Baker Dam | 14
Vancouver | 22
Vashon Island | 28
Walla Walla AP | 6
Walla Walla CO | 13
Wapato | 10
Washougal 8 ENE | 21
Waterville | 1
Wawawai 2 NW | 14
Wellpinit | 1
Wenatchee AP | 13
Wenatchee CO | 10
West Clarkston | 10
Whidbey Island | 11
White River RS | 12
White Swan RS | 8
Whitman Mission | 11
Wilbur | 4
Willapa Harbor | 26
Wilson Creek | 3
Wind River | 15
Winthrop 1 WSW | -12
Yakima AP | 11

## Below Grade Walls & Slabs (hidden)
WSU Code Compliance Calculator - WSEC 2015 &2018 | [5 empty] | (C) 2020
Below Grade Walls and Slabs - Updated to WSEC 2018, Appendix A, Table A104.1 (values changed from WSEC 2015 Appendix A)
Index |  | Component Description | Reference | Wall U | Slab F
1
2 |  | === Most Frequently Used =========
3 | 2' depth | R0 Uninsulated, 2' depth | 10-1 | 0.331 | 0.58 | Updated to WSEC 2018
4 | 2' depth | R10 Foam Ext, 2' depth | 10-1 | 0.271 | 0.51 | Updated to WSEC 2018
5 | 2' depth | R11 Batt, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.185 | 0.43 | Updated to WSEC 2018
6 | 2' depth | R12 Foam Ext, 2' depth | 10-1 | 0.040337 | 0.47 | Updated to WSEC 2018
7 | 2' depth | R13 Batt + R5 ci, 2' depth | Interpolated between R11 and R19 | 0.040337 | 0.67866
8 | 2' depth | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | 10-1 | 0.055 | 0.293 | Added 2020
9 | 2' depth | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.029 | 0.307 | Added 2020 from reference
10 | 2' depth | R21 Batt w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.032 | 0.505 | Updated to WSEC 2018
11 | 3.5' depth | R0 Uninsulated, 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.271 | 0.51 | Updated to WSEC 2018
12 | 3.5' depth | R10 Foam Ext, 3.5' depth | 10-1 | 0.075 | 0.52 | Updated to WSEC 2018
13 | 3.5' depth | R11 Batt, 3.5' depth | WSU | 0.058 | 0.61 | Updated to WSEC 2018
14 | 3.5' depth | R12 Foam Ext, 3.5' depth | WSU | 0.057 | 0.57 | Updated to WSEC 2018
15 | 3.5' depth | R13 Batt + R5 ci, 3.5' depth | Interpolated between R11 and R19 | 0.038337 | 0.626
16 | 3.5' depth | R10 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | WSU | 0.064 | 0.324 | Added 2020
17 | 3.5' depth | R20 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | WSU | 0.038 | 0.331 | Added 2020 from reference
18 | 3.5' depth | R21 Batt w/TB, 3.5' depth | WSU | 0.04 | 0.56 | Updated to WSEC 2018
19 | 7' depth | R0 Uninsulated, 7' depth | 10-1 | 0.185 | 0.43 | Updated to WSEC 2018
20 | 7' depth | R10 Foam Ext, 7' depth | 10-1 | 0.058 | 0.47 | Updated to WSEC 2018
21 | 7' depth | R11 Batt, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.051 | 0.541 | Updated to WSEC 2018
22 | 7' depth | R12 Foam Ext, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.05 | 0.42 | Updated to WSEC 2018
23 | 7' depth | R13 Batt + R5 ci, 7' depth | Interpolated between R11 and R19 | 0.034003 | 0.55633
24 | 7' depth | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.055 | 0.293 | Added 2020
25 | 7' depth | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | WSU | 0.034 | 0.304 | Added 2020 from reference
26 | 7' depth | R21 Batt w/TB, 7' depth | WSU | 0.035 | 0.5 | Updated to WSEC 2018
27 |  | =================================
28 | 2' depth | R0 Uninsulated, 2' depth | 10-1 | 0.331 | 0.58 | Updated to WSEC 2018
29 | 2' depth | R10 Foam Ext, 2' depth | 10-1 | 0.089 | 0.56 | Updated to WSEC 2018
30 | 2' depth | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.068 | 0.345 | Added 2020
31 | 2' depth | R11 Batt, 2' depth | 10-1 | 0.063 | 0.67 | Updated to WSEC 2018
32 | 2' depth | R11 Batt w/TB, 2' depth | 10-1 | 0.065 | 0.59 | Updated to WSEC 2018
33 | 2' depth | R11 Batt + R5 ci, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.044 | 0.677 | Added 2023 from reference
34 | 2' depth | R11 Batt + R5 ci w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.046 | 0.59 | Added 2020 from reference
35 | 2' depth | R11 Batt + R5 ci R10 Fully Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.048 | 0.348 | Added 2020 from reference
36 | 2' depth | R12 Foam Ext, 2' depth | 10-1 | 0.61 | 0.6 | Updated to WSEC 2018
37 | 2' depth | R13 Batt, 2' depth | WSU | 0.056007 | 0.67333 | Interpolated between R11 and R19
38 | 2' depth | R13 Batt w/TB , 2' depth | WSU | 0.05834 | 0.59 | Interpolated between R11 and R19
39 | 2' depth | R13 Batt + R5 ci, 2' depth | WSU | 0.040337 | 0.67866 | Interpolated between R11 and R19
40 | 2' depth | R15 Batt, 2' depth | WSU | 0.0525 | 0.675 | Interpolated between R11 and R19
41 | 2' depth | R15 Batt w/TB, 2' depth | WSU | 0.055 | 0.59 | Interpolated between R11 and R19
42 | 2' depth | R19 Batt, 2' depth | 10-1 | 0.042 | 0.68 | Updated to WSEC 2018
43 | 2' depth | R19 Batt w/TB, 2' depth | 10-1 | 0.045 | 0.59 | Updated to WSEC 2018
44 | 2' depth | R19 Batt + R5 ci, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.033 | 0.682 | Added 2023 from reference
45 | 2' depth | R19 Batt + R5 ci w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.034 | 0.594 | Added 2023 from reference
46 | 2' depth | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.04 | 0.35 | Added 2020 from reference
47 | 2' depth | R21 Batt, 2' depth | WSU | 0.04 | 0.68 | Updated to WSEC 2018
48 | 2' depth | R21 Batt w/TB, 2' depth | WSU | 0.042 | 0.59 | Updated to WSEC 2018
49 | 2' depth | R21 Batt + R5 ci, 2' depth | 10-1 | 0.031 | 0.68 | Added in WSEC 2018
50 | 2' depth | R21 Batt + R5 ci w/TB, 2' depth | 10-1 | 0.032 | 0.59 | Added in WSEC 2018
51 | 2' depth | R21 Batt + R7 ci, 2' depth | 10-1 | 0.029 | 0.68 | Added in WSEC 2018
52 | 2' depth | R21 Batt + R7 ci w/TB, 2' depth | 10-1 | 0.03 | 0.59 | Added in WSEC 2018
53 | 2' depth | R21 Batt + R5 ci R10 Fully Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.031 | 0.35 | Added 2020 from reference
54 | 2' depth | R25 Batt w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.593 | Added 2020 from reference
55 | 2' depth | R25 Batt w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.04 | 0.35 | Added 2020 from reference
56 | 3.5' depth | R0 Uninsulated, 3.5' depth | 10-1 | 0.271 | 0.51 | Updated to WSEC 2018
57 | 3.5' depth | R11 Batt 3.5' depth | 10-1 | 0.075 | 0.52 | Updated to WSEC 2018
58 | 3.5' depth | R11 Batt 3.5' depth w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.064 | 0.324 | Added 2020
59 | 3.5' depth | R11 Batt + R5 ci 3.5' depth | 10-1 | 0.058 | 0.61 | Updated to WSEC 2018
60 | 3.5' depth | R11 Batt + R5 ci 3.5' depth w/TB | 10-1 | 0.061 | 0.55 | Updated to WSEC 2018
61 | 3.5' depth | R11 Batt + R5 ci 3.5' depth R10 Fully Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.042 | 0.624 | Added 2023 from reference
62 | 3.5' depth | R13 Batt 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.043 | 0.553 | Added 2020 from reference
63 | 3.5' depth | R13 Batt + R5 ci 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.045 | 0.329 | Added 2020 from reference
64 | 3.5' depth | R13 Batt 3.5' depth w/TB | 10-1 | 0.057 | 0.57 | Updated to WSEC 2018 | [7 empty] | Figures from: Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf
65 | 3.5' depth | R15 Batt 3.5' depth | WSU | 0.052339 | 0.61333 | Interpolated between R11 and R19
66 | 3.5' depth | R15 Batt 3.5' depth w/TB | WSU | 0.054673 | 0.55 | Interpolated between R11 and R19
67 | 3.5' depth | R19 Batt 3.5' depth | WSU | 0.038337 | 0.626 | Interpolated between R11 and R19
68 | 3.5' depth | R19 Batt w/TB, 3.5' depth | WSU | 0.0495 | 0.615 | Interpolated between R11 and R19
69 | 3.5' depth | R19 Batt + R5 ci 3.5' depth | WSU | 0.0515 | 0.55 | Interpolated between R11 and R19
70 | 3.5' depth | R19 Batt + R5 ci 3.5' depth w/TB | 10-1 | 0.041 | 0.62 | Updated to WSEC 2018
71 | 3.5' depth | R21 Batt 3.5' depth | 10-1 | 0.042 | 0.55 | Updated to WSEC 2018
72 | 3.5' depth | R21 Batt 3.5' depth w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.031 | 0.63 | Added 2023 from reference
73 | 3.5' depth | R21 Batt + R5 ci 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.033 | 0.558 | Added 2023 from reference
74 | 3.5' depth | R21 Batt + R5 ci 3.5' depth w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.331 | Added 2020 from reference
75 | 3.5' depth | R21 Batt + R7 ci 3.5' depth | WSU | 0.038 | 0.63 | Updated to WSEC 2018
76 | 3.5' depth | R21 Batt + R7 ci 3.5' depth w/TB | WSU | 0.04 | 0.56 | Updated to WSEC 2018
77 | 3.5' depth | R21 Batt + R5 ci 3.5' depth R10 Fully Underslab | 10-1 | 0.03 | 0.632 | Added in WSEC 2018
78 | 3.5' depth | R25 Batt 3.5' depth w/TB | 10-1 | 0.031 | 0.56 | Added in WSEC 2018
79 | 3.5' depth | R25 Batt 3.5' depth w/TB, R10 Full Underslab | 10-1 | 0.027 | 0.63 | Added in WSEC 2018
80 | 3.5' depth | R-20 perimeter, 3.5' depth w/TB, R10 Full Underslab | 10-1 | 0.029 | 0.56 | Added in WSEC 2018
81 | 3.5' depth | R10 Foam Ext 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.032 | 0.333 | Added 2020 from reference
82 | 3.5' depth | R12 Foam Ext 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.036 | 0.557 | Added 2020 from reference
83 | 3.5' depth | R10 Perimeter 3.5' depth w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.331 | Added 2020 from reference
84 | 7' depth | R0 Uninsulated, 7' depth | 10-1 | 0.185 | 0.43 | Updated to WSEC 2018
85 | 7' depth | R10 Foam Ext, 7' depth | 10-1 | 0.058 | 0.47 | Updated to WSEC 2018
86 | 7' depth | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.055 | 0.293 | Added 2020
87 | 7' depth | R11 Batt, 7' depth | 10-1 | 0.051 | 0.541 | Updated to WSEC 2018
88 | 7' depth | R11 Batt w/TB, 7' depth | 10-1 | 0.053 | 0.49 | Updated to WSEC 2018
89 | 7' depth | R11 Batt + R5 ci, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.037 | 0.553 | Added 2023 from reference
90 | 7' depth | R11 Batt + R5 ci w/TB, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.499 | Added 2020 from reference
91 | 7' depth | R11 Batt + R5 ci R10 Fully Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.04 | 0.301 | Added 2020 from reference
92 | 7' depth | R12 Foam Ext, 7' depth | 10-1 | 0.05 | 0.42 | Updated to WSEC 2018
93 | 7' depth | R13 Batt, 7' depth | WSU | 0.046005 | 0.54067 | Interpolated between R11 and R19
94 | 7' depth | R13 Batt w/TB , 7' depth | WSU | 0.047672 | 0.49333 | Interpolated between R11 and R19
95 | 7' depth | R13 Batt + R5 ci, 7' depth | WSU | 0.034003 | 0.55633 | Interpolated between R11 and R19
96 | 7' depth | R15 Batt, 7' depth | WSU | 0.0435 | 0.5405 | Interpolated between R11 and R19
97 | 7' depth | R15 Batt w/TB, 7' depth | WSU | 0.045 | 0.495 | Interpolated between R11 and R19
98 | 7' depth | R19 Batt, 7' depth | 10-1 | 0.036 | 0.54 | Updated to WSEC 2018
99 | 7' depth | R19 Batt w/TB, 7' depth | 10-1 | 0.037 | 0.5 | Updated to WSEC 2018
100 | 7' depth | R19 Batt + R5 ci, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.028 | 0.563 | Added 2023 from reference
101 | 7' depth | R19 Batt + R5 ci w/TB, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.029 | 0.507 | Added 2023 from reference
102 | 7' depth | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.034 | 0.304 | Added 2020 from reference
103 | 7' depth | R21 Batt, 7' depth | WSU | 0.035 | 0.56 | Updated to WSEC 2018
104 | 7' depth | R21 Batt w/TB, 7' depth | WSU | 0.035 | 0.5 | Updated to WSEC 2018
105 | 7' depth | R21 Batt + R5 ci, 7' depth | 10-1 | 0.027 | 0.56 | Added in WSEC 2018
106 | 7' depth | R21 Batt + R5 ci w/TB, 7' depth | 10-1 | 0.028 | 0.51 | Added in WSEC 2018
107 | 7' depth | R21 Batt + R7 ci, 7' depth | 10-1 | 0.025 | 0.57 | Added in WSEC 2018
108 | 7' depth | R21 Batt + R7 ci w/TB, 7' depth | 10-1 | 0.026 | 0.57 | Added in WSEC 2018
109 | 7' depth | R21 Batt + R5 ci R10 Fully Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.029 | 0.307 | Added 2020 from reference
110 | 7' depth | R25 Batt w/TB, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.032 | 0.505 | Added 2020 from reference
111 | 7' depth | R25 Batt w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.034 | 0.304 | Added 2020 from reference
112 | Depth | == Custom Entries per WSEC R402.1.5 U-factor Reference and Calculations ======== |  | Wall U | Slab F | Notes
113 |  | Test slab | Custom | 0.05 | 0.5
114 |  |  | Custom
115 |  |  | Custom
116 |  |  | Custom
117 |  |  | Custom
118 |  |  | Custom
119 |  |  | Custom
120 |  |  | Custom
If you rearrange, add or delete rows below -- be sure to make corresponding changes to the six areas above.
|  | DropDown_BelowGradeSlab |  |  | Component Description | Wall U | Slab F | Component Description | Wall U | Slab F | Component Description | Wall U | Slab F
1 |  |  | Reference | Notes | 2' depth |  |  | 3.5' depth |  |  | 7' depth
2 |  | === Most Frequently Used =========
3 |  | R0 Uninsulated | 10-1 | Updated to WSEC 2018 | R0 Uninsulated, 2' depth | 0.331 | 0.58 | R0 Uninsulated, 3.5' depth | 0.271 | 0.51 | R0 Uninsulated, 7' depth | 0.185 | 0.43
4 |  | R10 Foam Ext | 10-1 | Updated to WSEC 2018 | R10 Foam Ext, 2' depth | 0.089 | 0.56 | R10 Foam Ext, 3.5' depth | 0.075 | 0.52 | R10 Foam Ext, 7' depth | 0.058 | 0.47
5 |  | R11 Batt | 10-1 | Updated to WSEC 2018 | R11 Batt, 2' depth | 0.063 | 0.67 | R11 Batt, 3.5' depth | 0.058 | 0.61 | R11 Batt, 7' depth | 0.051 | 0.541
6 |  | R12 Foam Ext | 10-1 | Updated to WSEC 2018 | R12 Foam Ext, 2' depth | 0.61 | 0.6 | R12 Foam Ext, 3.5' depth | 0.057 | 0.57 | R12 Foam Ext, 7' depth | 0.05 | 0.42
7 |  | R13 Batt + R5 ci | WSU | Interpolated between R11 and R19 | R13 Batt + R5 ci, 2' depth | 0.040337 | 0.67866 | R13 Batt + R5 ci, 3.5' depth | 0.038337 | 0.626 | R13 Batt + R5 ci, 7' depth | 0.034003 | 0.55633
8 |  | R10 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.068 | 0.345 | R10 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.064 | 0.324 | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.055 | 0.293
9 |  | R20 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.04 | 0.35 | R20 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.038 | 0.331 | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.034 | 0.304
10 |  | R19 Batt w/TB | 10-1 | Updated to WSEC 2018 | R19 Batt w/TB, 2' depth | 0.045 | 0.59 | R19 Batt w/TB, 3.5' depth | 0.042 | 0.55 | R19 Batt w/TB, 7' depth | 0.037 | 0.5
11 |  | R21 Batt w/TB | WSU | Updated to WSEC 2018 | R21 Batt w/TB, 2' depth | 0.042 | 0.59 | R21 Batt w/TB, 3.5' depth | 0.04 | 0.56 | R21 Batt w/TB, 7' depth | 0.035 | 0.5
12 |  | ============================
13 |  | R0 Uninsulated | 10-1 | Updated to WSEC 2018 | R0 Uninsulated, 2' depth | 0.331 | 0.58 | R0 Uninsulated, 3.5' depth | 0.271 | 0.51 | R0 Uninsulated, 7' depth | 0.185 | 0.43
14 |  | R10 Foam Ext | 10-1 | Updated to WSEC 2018 | R10 Foam Ext, 2' depth | 0.089 | 0.56 | R10 Foam Ext, 3.5' depth | 0.075 | 0.52 | R10 Foam Ext, 7' depth | 0.058 | 0.47
15 |  | R10 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.068 | 0.345 | R10 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.064 | 0.324 | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.055 | 0.293
16 |  | R11 Batt | 10-1 | Updated to WSEC 2018 | R11 Batt, 2' depth | 0.063 | 0.67 | R11 Batt, 3.5' depth | 0.058 | 0.61 | R11 Batt, 7' depth | 0.051 | 0.541
17 |  | R11 Batt w/TB | 10-1 | Updated to WSEC 2018 | R11 Batt w/TB, 2' depth | 0.065 | 0.59 | R11 Batt w/TB, 3.5' depth | 0.061 | 0.55 | R11 Batt w/TB, 7' depth | 0.053 | 0.49
18 |  | R11 Batt + R5 ci | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2023 from reference | R11 Batt + R5 ci, 2' depth | 0.044 | 0.677 | R11 Batt + R5 ci, 3.5' depth | 0.042 | 0.624 | R11 Batt + R5 ci, 7' depth | 0.037 | 0.553
19 |  | R11 Batt + R5 ci w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R11 Batt + R5 ci w/TB, 2' depth | 0.046 | 0.59 | R11 Batt + R5 ci w/TB, 3.5' depth | 0.043 | 0.553 | R11 Batt + R5 ci w/TB, 7' depth | 0.038 | 0.499
20 |  | R11 Batt + R5 ci R10 Fully Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R11 Batt + R5 ci R10 Fully Underslab, 2' depth | 0.048 | 0.348 | R11 Batt + R5 ci R10 Fully Underslab, 3.5' depth | 0.045 | 0.329 | R11 Batt + R5 ci R10 Fully Underslab, 7' depth | 0.04 | 0.301
21 |  | R12 Foam Ext | 10-1 | Updated to WSEC 2018 | R12 Foam Ext, 2' depth | 0.61 | 0.6 | R12 Foam Ext, 3.5' depth | 0.057 | 0.57 | R12 Foam Ext, 7' depth | 0.05 | 0.42
22 |  | R13 Batt | WSU | Interpolated between R11 and R19 | R13 Batt, 2' depth | 0.056007 | 0.67333 | R13 Batt, 3.5' depth | 0.052339 | 0.61333 | R13 Batt, 7' depth | 0.046005 | 0.54067
23 |  | R13 Batt w/TB | WSU | Interpolated between R11 and R19 | R13 Batt w/TB , 2' depth | 0.05834 | 0.59 | R13 Batt w/TB , 3.5' depth | 0.054673 | 0.55 | R13 Batt w/TB , 7' depth | 0.047672 | 0.49333
24 |  | R13 Batt + R5 ci | WSU | Interpolated between R11 and R19 | R13 Batt + R5 ci, 2' depth | 0.040337 | 0.67866 | R13 Batt + R5 ci, 3.5' depth | 0.038337 | 0.626 | R13 Batt + R5 ci, 7' depth | 0.034003 | 0.55633
25 |  | R15 Batt | WSU | Interpolated between R11 and R19 | R15 Batt, 2' depth | 0.0525 | 0.675 | R15 Batt, 3.5' depth | 0.0495 | 0.615 | R15 Batt, 7' depth | 0.0435 | 0.5405
26 |  | R15 Batt w/TB | WSU | Interpolated between R11 and R19 | R15 Batt w/TB, 2' depth | 0.055 | 0.59 | R15 Batt w/TB, 3.5' depth | 0.0515 | 0.55 | R15 Batt w/TB, 7' depth | 0.045 | 0.495
27 |  | R19 Batt | 10-1 | Updated to WSEC 2018 | R19 Batt, 2' depth | 0.042 | 0.68 | R19 Batt, 3.5' depth | 0.041 | 0.62 | R19 Batt, 7' depth | 0.036 | 0.54
28 |  | R19 Batt w/TB | 10-1 | Updated to WSEC 2018 | R19 Batt w/TB, 2' depth | 0.045 | 0.59 | R19 Batt w/TB, 3.5' depth | 0.042 | 0.55 | R19 Batt w/TB, 7' depth | 0.037 | 0.5
29 |  | R19 Batt + R5 ci | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2023 from reference | R19 Batt + R5 ci, 2' depth | 0.033 | 0.682 | R19 Batt + R5 ci, 3.5' depth | 0.031 | 0.63 | R19 Batt + R5 ci, 7' depth | 0.028 | 0.563
30 |  | R19 Batt + R5 ci w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2023 from reference | R19 Batt + R5 ci w/TB, 2' depth | 0.034 | 0.594 | R19 Batt + R5 ci w/TB, 3.5' depth | 0.033 | 0.558 | R19 Batt + R5 ci w/TB, 7' depth | 0.029 | 0.507
31 |  | R20 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.04 | 0.35 | R20 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.038 | 0.331 | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.034 | 0.304
32 |  | R21 Batt | WSU | Updated to WSEC 2018 | R21 Batt, 2' depth | 0.04 | 0.68 | R21 Batt, 3.5' depth | 0.038 | 0.63 | R21 Batt, 7' depth | 0.035 | 0.56
33 |  | R21 Batt w/TB | WSU | Updated to WSEC 2018 | R21 Batt w/TB, 2' depth | 0.042 | 0.59 | R21 Batt w/TB, 3.5' depth | 0.04 | 0.56 | R21 Batt w/TB, 7' depth | 0.035 | 0.5
34 |  | R21 Batt + R5 ci | 10-1 | Added in WSEC 2018 | R21 Batt + R5 ci, 2' depth | 0.031 | 0.68 | R21 Batt + R5 ci, 3.5' depth | 0.03 | 0.632 | R21 Batt + R5 ci, 7' depth | 0.027 | 0.56
35 |  | R21 Batt + R5 ci w/TB | 10-1 | Added in WSEC 2018 | R21 Batt + R5 ci w/TB, 2' depth | 0.032 | 0.59 | R21 Batt + R5 ci w/TB, 3.5' depth | 0.031 | 0.56 | R21 Batt + R5 ci w/TB, 7' depth | 0.028 | 0.51
36 |  | R21 Batt + R7 ci | 10-1 | Added in WSEC 2018 | R21 Batt + R7 ci, 2' depth | 0.029 | 0.68 | R21 Batt + R7 ci, 3.5' depth | 0.027 | 0.63 | R21 Batt + R7 ci, 7' depth | 0.025 | 0.57
37 |  | R21 Batt + R7 ci w/TB | 10-1 | Added in WSEC 2018 | R21 Batt + R7 ci w/TB, 2' depth | 0.03 | 0.59 | R21 Batt + R7 ci w/TB, 3.5' depth | 0.029 | 0.56 | R21 Batt + R7 ci w/TB, 7' depth | 0.026 | 0.57
38 |  | R21 Batt + R5 ci R10 Fully Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R21 Batt + R5 ci R10 Fully Underslab, 2' depth | 0.031 | 0.35 | R21 Batt + R5 ci R10 Fully Underslab, 3.5' depth | 0.032 | 0.333 | R21 Batt + R5 ci R10 Fully Underslab, 7' depth | 0.029 | 0.307
39 |  | R25 Batt w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R25 Batt w/TB, 2' depth | 0.038 | 0.593 | R25 Batt w/TB, 3.5' depth | 0.036 | 0.557 | R25 Batt w/TB, 7' depth | 0.032 | 0.505
40 |  | R25 Batt w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R25 Batt w/TB, R10 Full Underslab, 2' depth | 0.04 | 0.35 | R25 Batt w/TB, R10 Full Underslab, 3.5' depth | 0.038 | 0.331 | R25 Batt w/TB, R10 Full Underslab, 7' depth | 0.034 | 0.304
41 |  | == Custom Entries per WSEC R402.1.5 U-factor Reference and Calculations ======== |  |  |  | Wall U | Slab F
42 |  |  | Custom
43 |  |  | Custom
44 |  |  | Custom
45 |  |  | Custom
46 |  |  | Custom
47 |  |  | Custom
48 |  |  | Custom
49 |  |  | Custom
======================
Note on C5: On each data tab we have created a “Most Frequently Used” section at the top, which appears on drop down menus and includes the most commonly selected items. Most of the items in this top section are intentionally duplicates of items from the more extensive list below.
Note on C138: On each data tab we have created a “Most Frequently Used” section at the top, which appears on drop down menus and includes the most commonly selected items. Most of the items in this top section are intentionally duplicates of items from the more extensive list below.
Note on F138: On each data tab we have created a “Most Frequently Used” section at the top, which appears on drop down menus and includes the most commonly selected items. Most of the items in this top section are intentionally duplicates of items from the more extensive list below.
Editing Instructions:
Only white areas on the sheet can be edited. Do not delete rows, columns or cells. This will disrupt the indexing reference to the companion worksheet.
Enter component description, and calculated U-factor. Submit the detailed calculations as part of the application for your building permit.
Where proposed construction assemblies are not represented in Appendix A tables, values shall be calculated in accordance with Chapters 21-29 in Standard RS-1 listed in Chapter 5, (ASHRAE Handbook of Fundamentals) using the framing factors listed in Appendix A where applicable.
For envelope assemblies containing metal framing, the U-factor shall be determined by one of the following methods:
1. Results of laboratory or field measurements.
2. Standard RS-25, listed in Chapter 5, where the metal framing is bonded on one or both sides to a metal skin or covering.
3. The zone method as provided in Chapter 24 of Standard RS-1, listed in Chapter 5.
4. Results of parallel path correction factors for effective framing/cavity R-values as provided in TABLE A103.3.6.1(1) : Effective R-Values for Metal Framing and Cavity Only for metal stud walls and roof/ceilings.
Return to Input